CALIFORNIA STATE POLYTECHNIC UNIVERSITY, POMONA

ENVIRONMENTAL HEALTH & SAFETY

PROJECT PLAN REVIEW CHECKLIST

February 12, 2008

Environmental Health & Safety (EH&S) developed this checklist for internal use by EH&S and Facilities Planning & Management staff when reviewing plans/projects.  EH&S believes this checklist is consistent with current government regulations.  However, all regulations are subject to interpretation by visiting inspectors.  EH&S cannot guarantee that completion of this checklist ensures regulatory compliance.  This checklist was developed to provide guidance rather than prescribe requirements.  It is not all inclusive and should be augmented as necessary according to site-specific conditions.

Project:

| Phase: (check box) | Schematic | Type: (check box) | New Construction |
| --- | --- | --- | --- |
|  | Preliminary |  | Renovation |
|  | Working Drawings |  | Demolition |
|  | Other_________________(specify) |  |  |

Signature:								Date:

HAZARDOUS MATERIALS

Asbestos

- Do any of the existing building materials contain asbestos including, but not limited to:  (a) wall plaster; (b) vinyl floor tile and mastic; (c) ceiling tile; (d) counter tops; (e) fume hoods; (f) doors; (g) piping; (h) pipe insulation; (i) fireproofing; and/or (j) sprayed acoustic ceilings?  If so, will the asbestos materials be directly or inadvertently disturbed during renovation/demolition?

- An asbestos survey is required by law prior to renovation/demolition and is a means of practically estimating the cost of abatement and disposal.  The project specifications should identify the following:  (a) asbestos areas; (b) abatement requirements; (c) third-party monitoring; (d) replacement materials to be specified as substitutes for the asbestos removed; (e) asbestos handling procedures; (f) a disposal location acceptable to the Environmental Health & Safety Department; and (g) notification to the local air quality management district and other agencies requiring asbestos abatement notification.

- Asbestos containing materials should not be used for any replacement material.  The Project Architect shall submit a letter verifying that all materials are asbestos free to Environmental Health & Safety.

- Seriously consider the removal of all asbestos containing materials in areas of a building.  Leaving asbestos containing materials in buildings costs the University more money over the life time of the building to maintain the building.  This is especially true of asbestos containing fire-proofing in crawl spaces were utilities are located and sprayed acoustic ceilings.

# Lead (Pb)-Containing Materials

- Based on the age of the buildings, proposed renovation operations may disturb painted/coated surfaces that contain lead.  Have funds been allocated for lead-based paint testing of the affected areas?  Once  it is determined that lead is present, the campus is required to warn the contractor that such a hazard exists.  Lead hazard warning language should be included in the contractor bid package.  In such cases, the contractor will be required to comply with Cal/OSHA’s Title 8 (Section 1532.1) “Lead in Construction” standard.  Have funds been allocated for these contractor costs?  In addition, if the lead content of the paint exceeds the Cal/EPA hazardous waste limits for lead, any debris that is discarded must be treated in accordance with Title 22.  Have funds been allocated for the disposal of any potential (lead containing) hazardous materials?

- Could non lead containing products be substituted and used instead of lead-containing products (e.g., red lead primer in steel coatings, lead solder) or best available control technology at the time?

- All building, plumbing and piping materials should be non lead-containing.

Polychlorinated Biphenyl (PCB)-Containing Material

- Has a survey been conducted to determine if PCB-containing material will be affected by the project (e.g., light ballast removal or replacement, transformer removal or replacement)?

EH&S Project Review Checklist

January 24, 2002

Page 2 of 7

- Have appropriate costs for such removal or replacement been included in the project cost estimate?

- PCB Breakers:  What is the concentration (in parts per million) of PCBs in the units?  This information will dictate the handling of the units as required by law.

- How will the following PCB waste issues be handled:  (a) light ballast removal; (b) transformer removal; (c) temporary storage; (d) disposal; (e) manifesting obligations; and (f) funding?

- Have appropriate disposal costs been included in the project cost estimate?

Hazardous Waste Disposal

- Has all the possible hazardous waste (e.g. asbestos, lead, PCB, etc.) that will be generated as a result of this project been identified?

- Has the campus EH&S Department been notified regarding the quantities and types of waste that will be generated by this project?

- Has the campus EH&S Department been notified to be available to coordinate hazardous waste disposal and sign hazardous waste manifests?  Twenty-four hour advance notice is required.

- Have funds been budget to reimburse the EH&S Department for the Hazardous Waste Generator Fee of $65 per ton.

- Have measures been taken to ensure the EH&S Department receives all copies of hazardous waste manifests, especially the signed manifest released by the treatment, storage and disposal facility?

- Have measures been taken to qualify hazardous waste contractors (e.g. asbestos or lead removal contractors) and provide copies of qualification packages to EH&S?

Custodial Closets/Rooms

- Will the building contain custodial closets/rooms?  If so, will the following hazardous materials be stored, mixed or used in the custodial closets/rooms:  (1) flammable materials; (2) pesticides; (3) corrosives; (4) irritants?  Will the custodial closets/rooms contain an emergency eyewash, storage cabinets for hazardous materials or a custodial utility sink?

- All chemical storage areas should meet UBC, UFC, and NFPA standards (e.g., design, chemical segregation/compatibility, secondary containment, explosion-proof lighting, drainage, fire wall rating, accessibility).

- Have provisions been made to accommodate segregation of incompatible hazardous substances within individual rooms?

- Use only the cleaning materials and equipment which are compatible with the surface being cleaned, as recommended by the manufacturer of the material or as approved by the Architect.

- Will Material Safety Data Sheets (MSDS) for all hazardous materials be provided?  Will EH&S be provided MSDS during the early planning or construction phase of this project?

- The project specifications should state that the contractor is responsible to make a copy of the following available to EH&S:  (a) the contractor’s Injury and Illness Prevention Program (IIPP) and/or Site Safety Plan; (b) an MSDS for each product the contractor plans to use on campus property; (c) other written EH&S programs as requested.

- Will processes or operations involving the handling and use of flammable and/or oxidizing materials (e.g., acetone, chlorates, peroxides) be grounded and bonded appropriately?  An effective grounding/bonding system should be provided whenever chemicals are transferred from one container to another.

- Will all plumbed emergency eyewash and deluge shower units meet the requirements of section 5, 7 or 9 of ANSI Z358.1 - 1981 and be provided at all work areas where, during routine operations or foreseeable emergencies, workers may come into contact with a substance which is corrosive or severely irritating to the skin or which is toxic by skin absorption?  Will these units be in accessible, unobstructed locations that require no more than 10 seconds for the injured person to reach and supply potable water at the flow rates and time duration specified in ANSI Z358.1 - 1981?  (8 CCR 5162).  All emergency eyewashs and deluge showers shall be equipped with a floor drain, which is flush with the floor.

EH&S Project Review Checklist

January 24, 2002

Page 3 of 7

AIR QUALITY

- “Permits to construct” should be obtained by the design contractor while the project is in the design stage. The Contractor will provide permits to operate to the University upon completion of the Project.  Unless specified in a permit exemption rule by the applicable air district, all fuel combustion equipment (boilers, internal combustion engine-type of equipment, kilns, turbines, water heaters, etc.); spray booths; HEPA vacuums; mercury vacuums, etc.; degreasers; asphalt mixing units; and air pollution control devices, such as filters, scrubbers, baghouses, afterburners will require permits and/or registration under Rule 222.  EH&S Air Permitting procedures are available on the web at

http://www.cpp.edu/~ehs/files/occupational/doc/AirPermitProcedures.doc.

- Are mechanisms in place to ensure that EH&S will receive copies of all permits?

- Check BACT requirements for all new equipment and air pollution controls emitting air pollutants.

- Incorporate upcoming air quality equipment and compliance standards into renovation and new construction projects.  Consult the campus EH&S Department.

- Check for the following construction dust control measures: (a) chemical/water suppression; (b) cover storage piles; (c) cost of new vegetation and mulch stabilizers; (d) particulate matter monitoring and recordkeeping; and (e) control measures beyond CEQA mitigation.

- Verify that proposed project paints and cleaning products meet air quality requirements for volatile organic compound (VOC) content.  Verify with the local air district regarding restrictions on solvent (degreaser)/toxic air contaminant/VOC/CFC and HCFC limitations for content and usage.  Provide EH&S Department with amounts of VOCs, emission factors and dates used for completion of annual emissions report for the campus.

- Check the type of refrigerants specified for chillers, and other refrigeration equipment, etc.  Do not specify the use of CFC-11 or 12 or other class I substances and avoid, if possible, class II substances (see Federal Clean Air Act Amendments of 1990).

- Use non-diesel fuels for backup equipment or emergency equipment whenever feasible.

HVAC

- Will the exhaust system’s discharge be located an effectively safe distance from building outdoor air intakes?

- Will fume hood exhaust diffusers be located in an area which prevents lab exhaust air from being pulled into building return or outside air systems?

- Will the fume hood rooftop exhaust stacks extend at least seven (7) feet above the roof and discharge vertically upward [8 CCR 5154.1(e)(4)(D)]?  For rain protection, high velocity discharge or concentric-duct, self-draining stacks (see Figure V-9, 8 CCR 5154.1) or their equivalent could be used.  Rain caps which divert the exhaust toward the roof are prohibited by code.

- Ensure that outdoor air intakes are located away from any possible sources of hazardous materials, biological materials or odors (e.g., loading docks, trash/refuse areas, boiler or fuel combustion equipment exhaust stacks and/ or catch basins).

- The ventilation rates for various areas within each building should comply with ASHRAE 62-89 standards.

- HVAC equipment (such as cooling towers, chillers and boilers) should be protected from both weather damage and animals/birds.  If this HVAC equipment is located outdoors, control measures should be in place that:  (a) minimize salt water corrosion of equipment; (b) minimize damage from excessive weather conditions; and (c) prevent animals and birds from building nests in or near equipment.  For example, birds that nest in HVAC equipment may create a housekeeping problem (bird droppings and feathers) and/or potential indoor air quality problems.

- Will kitchen exhaust ventilation be separate from the building’s ventilation system?  Will the kitchen’s exhaust be located away from the building outdoor air intakes?

- Will time be allowed for vapor off-gassing (from new equipment, carpets, wall coverings, paints, etc.) prior to occupancy?

EH&S Project Review Checklist

January 24, 2002

Page 4 of 7

- Ensure that chemical/biological storage and work areas are under negative pressure.

- Ensure that appropriate ventilation is provided for isolated hazardous materials/waste areas.  This may include a separate system for areas that are not connected with the main building ventilation system (e.g. chemical storage/use rooms cabinets, solvent type part cleaners, rechargeable back up batteries, etc.).

FUME HOODS

- The fume hoods and filters shall be constructed of materials that are compatible with the chemicals that will be exhausted from them.

- The fume hood exhaust shall be located in an area which prevents lab exhaust air from being pulled into building return or outdoor air systems.

- Emergency eyewash and deluge showers shall be installed where required by 8 CCR 5162 and equipped with floor drains, which are flush to the floor.

- Will all fume hoods be equipped with a quantitative airflow monitor that continuously indicates whether air is flowing into the exhaust system during operation or an acceptable alarm system [8 CCR 5154.1(e)(3)]?

CONFINED SPACES

- The following rooms/areas are normally considered confined spaces if built as typically designed in the specifications:  (a) fire pump room; (b) telephone/electrical rooms; (c) elevator machine room; (d) elevator pits; or (e) security rooms.  Serious consideration should be given to including a second entrance/door into the room/area to eliminate the existence of confined space conditions.

- Consider installation of confined space controls to make designated areas safe for occupants.  Among other items, these could include the following:  (a) permanent gas detection system (strongly recommended); (b) phone communication system; (c) video cameras; (d) self-contained breathing apparatus; (e) first-aid kits; and (f) fire extinguishers.

- Consider the installation of access doors instead of manholes, if feasible.  Occupant rescue through doors is much easier than through manholes.

- EH&S recommends including detailed contractor confined space specifications in the pre-qualification and the construction “conduct of work” language.

UNDERGROUND/ABOVEGROUND  STORAGE TANKS

- Has a survey been conducted to determine if petroleum storage tanks (This includes automotive lifts, elevators, etc that have associated tanks or reservoirs) may be impacted by this project?

- Based upon this survey, will this impact consist of any contaminated soil?

- Will this impact consist of removal, replacement, or addition of either an aboveground or underground storage tank system?

- Have appropriate cost estimates for removal/disposal, replacement or addition of either storage tank system been included in the cost estimate?

- If a new tank system is to be added during the project, does the system meet applicable codes and regulations for above and underground tanks systems?  These tank systems should comply with design requirements being proposed by the federal and state government, and should be state-of-the-art at the time they are installed.

- Have alternative fuel supply/storage measures been evaluated (aside from fuel oil and UST or AST)?

FIRE AND LIFE SAFETY

- Are automatic dampers in place for non-rated ceilings (tied into the smoke alarm/detector)?

- Will emergency power back-up be provided to sensitive public, medical, research and storage areas (i.e. elevators, stairwells, ventilation in medical centers and animal labs, fume hood that contain sensitive chemical and biological experiments, and chemical storage areas)?

EH&S Project Review Checklist

January 24, 2002

Page 5 of 7

- Will the protection area per sprinkler for hydraulically designed systems in the H-3 occupancy area not exceed 100 square feet?  Will the water supplied to these areas have a minimum density of 0.3 gpm per square foot?  (NFPA 13 Table 4-2.2 and Figure 5-2.3)

- Are all fire detection, alarm and communication systems designed in accordance with appropriate NFPA and NEC requirements?  (NFPA 101, Section 7-6)

- Will portable fire extinguishers be provided, mounted, located and identified  so they are readily accessible to employees?  Will portable fire extinguishers be distributed for use by employees on Class A fires so that the travel distance for employees to any extinguisher is 75 feet or less?  On Class B fires so that the travel distance from the Class B hazard area to any extinguisher is 50 feet or less?  For Class C hazards on the basis of the appropriate pattern for the existing Class A or Class B hazards?  (8 CCR 6151(c) and (d))

- Will panic hardware be installed on exit doors of buildings where hazardous materials are used, handled or stored?  (NFPA 101, Section 5-2.1.7)

- Will illumination of “means of egress” and emergency lighting be provided (NFPA 101, Sections 5-8 and 5-9)?  The use of tritium (or other radioactive material) is not allowed; installation, disposal and maintenance of such lighting requires special permits and add significant additional costs.

- Does the design allow for private offices to open into suites, directly to the outside or into something other than directly into a main exit corridor?  This design eliminates the use of automatic door closures.

- Do sealants, caulking and all other building materials meet the state fire marshal requirements for flammable materials?

- Are stairwells protected by asbestos free fire doors?

ELECTRICAL

- Will stationary electrical equipment, such as refrigerators and ovens be equipment-grounded through hard wiring, where there is no need for GFCIs?

- Will ground fault circuit interrupters (GFCIs) be used in areas where moisture may be present (e.g., areas where sinks and outlets are in close proximity)?  GFCIs should be used on all laboratory benches and where portable or non-stationary equipment is used.  There should be no more than three duplex outlets per interrupter.  GFCIs should also be used near wet operations, such as sinks.  Locating the GFCI unit in a central location at the main electrical panel for the lab encourages prompt attention to standing line leaks and other potential problems in the system.  The use of no more than three duplex outlets placed close to each other and attached to a GFCI on the same bench is ideal because this arrangement minimizes long wire runs with many junction boxes that have a leak potential.  In addition, when ground faults occur that shut the system down, they can be corrected easily and the system turned back on again quickly (Guidelines for Laboratory Design by Lou Diberardinis, et. al.).

PLUMBING

- Have design measures been taken to ensure that hazardous materials and wastes cannot reach either the sanitary sewer system or storm drain system during routine handling or accidental spillage?  All connections to both systems could be eliminated wherever hazardous materials or wastes are used, handled or stored.

- Install floor drains, which are flush with the floor, for water collection from emergency deluge showers.

- Are sump/holding tanks required/recommended for the (potential) effluent from hazardous materials storage and/or  emergency response areas?

- Consider sills, burms and liquid tight floors for areas where hazardous materials are stored and/or handled (e.g. laboratories, stockrooms, chiller rooms, maintenance shops, elevator rooms, etc.).

COMPUTER/INFORMATION SYSTEMS

- Will computers be repaired and maintained in the Information Center?  If so, will the Information Center have a computer maintenance shop?  Will chemical cleaners be used, handled or stored in such an area?  Will adequate ventilation be provided for solvent vapors?  Will appropriate storage cabinets be provided for chemicals?

- Are computer cabling trays easily accessible and designed (sized) to accommodate future expansion?

EH&S Project Review Checklist

January 24, 2002

Page 6 of 7

FOOD SERVICE AREA

- Will the food service area contain food preparation equipment such as grills or deep fat fryers?  If so, appropriate air quality permits shall be obtained and the installation of this equipment done in accordance with NFPA 96.  Will appropriate ventilation be provided?

- Will adequate occupant seating be provided in this area?

- Will exits be clearly marked?

SHIPPING RECEIVING AREAS (LOADING DOCKS)

- The shipping/receiving area should be designed for proper vehicle clearance and access.  Will the access lane(s) provide adequate room for vehicles to:  (a) enter; (b) load; and (c) turn around and/or back out?

- Are utility lines and pipes (e.g. natural gas lines) protected from vehicular impact by posts or other means?

- Will a telephone be located in the receiving area?

- Will the receiving area be well lit for night deliveries?

- Are removalable guard rails provided as required by Cal OSHA in 8 CCR 3209 and 3210?

- Are staging areas available for incompatible hazardous materials?

- Is refrigerator storage available for materials that require refrigeration upon delivery?  Is the refrigeration storage capacity adequate for anticipated deliveries?

- Shipping/receiving areas that receive hazardous materials should be equipped with fire extinguishers and an emergency eyewash and shower.

TRAFFIC CONTROL

- Have provisions been made for safe truck and heavy equipment access to the construction site?

- Have provisions been made for pedestrian safety (i.e., a fence around the construction site to exclude students, vendors and other public visitors)?

- If building occupants are allowed to pass through and/or work in the vicinity of the construction site, have provisions been made to ensure their safety and health?

OTHER

- Will tritium gas filled exit signs be disturbed during renovation activities?  If so, have removal and/or replacement of existing tritium exit signs, with non-tritium signs, been considered as part of this project?

- Will the height levels of illuminated exit signs meet the state fire marshal requirements?

- Consider alternative fuels for backup equipment and/or emergency equipment.

- Are the walks and paving designed to meet Cal/OSHA Title 8, GISO (sections 3214 and 3231), Americans with Disabilities Act requirements and NFPA 101 requirements for stairs and handrails?

- Are stairs designed to meet Cal/OSHA Title 8, GISO (sections 3214 and 3231) and NFPA 101 requirements for stairs and handrails?

- Do the vehicle lifts in the Transportation and Power Laboratory meet the California Occupational Safety and Health Administration (Cal/OSHA) requirements for automotive lifts (8 CCR 3540 et. seq.)?

- Will old carpeting, equipment and/or materials be recycled?

EH&S Project Review Checklist

January 24, 2002

Page 7 of 7

- Will the location of emergency eyewash/showers and drains be identified and/or marked on the space information descriptions?

- Has the design considered Cal/OSHA recommendations regarding issues associated with workplace violence?

- The campus may need to obtain a Storm Water Discharge Permit (SWDP) from the Regional Water Control Board.  Usually, a SWDP is required for any construction activity involving one acre or more of land prior to construction beginning.  In the case that a permit is required, permit fees and procedures should be included in the construction phase.

- Corridors/halls should be wide enough to accommodate both occupant traffic and potential art displays/exhibits in accordance with NFPA 101.

- Is adequate storage space allotted for routine maintenance items (i.e., ladders or tools)?  These maintenance items should be stored in designated maintenance storage areas.  They should not be stored in electrical or phone rooms/areas.

- Ensure that all required permits have been acquired (e.g., elevators, trenching, air quality).  Have funds been allocated for these permits?

ADMINISTRATIVE

- Has the campus EH&S Department been given the opportunity to review appropriate plans and specifications?

- Contact and review comments with the campus EH&S Department, if necessary.

- Have equipment warranties, project schematics and operational manuals been duly filed and transferred to the user?  Are the warranties current when the project is completed and turned over to the campus?

- Have building “as-builts” been updated?

- Have all required permits and funding sources for equipment/materials been identified prior to construction/ renovation?

- Has a EH&S been notified to verify all necessary permits are obtained prior to building occupancy?

Comments:

Filename: projrev.doc